# Appendix A

# Weekly Fire Code Review

Contractor:

Location(s):

Contractor Fire Prevention Program Superintendent:

Campus Fire Prevention Program Manager: Code Enforcement Official (CEO):

| # | All bracketed references are from NFPA 241, Standard for Safeguarding Construction, Alteration, and Demolition Operations, unless otherwise noted. This is not a complete list of requirements. | YES | NO | N/A |
| --- | --- | --- | --- | --- |
| 1 | Temporary Separation Walls {8.6.2}: Is there adequate separation between the work area and the rest of the building (One hour separation walls and 45 min opening protectives are often required by 8.6.2)? |  |  |  |
| 2 | Temporary Enclosures {4.3.1}: Are all panels, tarps, plastic sheeting, etc. flame retardant? |  |  |  |
| 3 | Impairments {FCNYS Section Chapter 9}: |  |  |  |
|  | Have paths of egress from occupied areas been maintained? |  |  |  |
|  | If fire alarm/detection systems in occupied areas have been temporarily impaired. Has the Campus Fire Prevention Program Manager approved the impairments/restrictions? {FCNYS Section 901} |  |  |  |
| 4 | Fire Extinguishers {4.3.4}: |  |  |  |
|  | Are appropriate fire extinguishers readily available, with a maximum travel distance of 50 feet? |  |  |  |
|  | Have fire extinguishers been provided within temporary enclosures? |  |  |  |
| 5 | Internal Combustion Devices {4.4}: |  |  |  |
|  | Are all internal combustion devices, where required, exhausted outside, with a least 9 inches between exhaust and combustible materials? |  |  |  |
|  | Is refueling only done on cool engines? |  |  |  |
| 6 | Temporary Heating {5.2}: Is temporary heating equipment listed and being used according to the manufacturer's requirements? |  |  |  |
| 7 | Hot Work Programs {5.1}: |  |  |  |
|  | Is there a current permit for ongoing operations? |  |  |  |
|  | Are all precautions required by the permit in place? |  |  |  |
|  | Is there a dedicated fire watch? |  |  |  |
|  | Does the fire watch extend after the completion for work (e.g., minimum of 30 min. in general or 2 hrs for roofs)? |  |  |  |
| 8 | Waste {5.4}: Are accumulations of waste materials, dust, and debris removed at the end of each shift (or more frequently as needed)? |  |  |  |
|  | Are materials subject to spontaneous ignition (e.g., oily rags) stored in listed disposal containers? |  |  |  |
| 9 | Trash Chutes {5.4}: Are trash chutes non-combustible, or provided with sprinkler protection? |  |  |  |
| 10 | Flammable/Combustible Liquids {5.5}: Are flammable/combustible liquids in proper containers and is there less than a total of 60 gallons inside and within 50 feet of the structure? |  |  |  |
| 11 | Compressed Gases { FCNYS Chapter 58}: Are compressed gases properly stored and being used? |  |  |  |

#	All bracketed references are from NFPA 241, Standard for Safeguarding Construction, Alteration, YES NO  N/A

and Demolition Operations, unless otherwise noted. This is not a completed list of requirements.

| 12 | Electrical {6.1}: |  |  |  |
| --- | --- | --- | --- | --- |
|  | Are extension cords rated and free from damage? |  |  |  |
|  | Do all branch circuits originate in approved power outlets or panel boards with over- current protection? |  |  |  |
|  | Are all circuits grounded? |  |  |  |
| 13 | Lighting {6.1.3}: |  |  |  |
|  | Do all temporary lights have guards? |  |  |  |
|  | Are lights only suspended by their cords when designated to be so suspended? |  |  |  |
|  | Are they fastened securely, if necessary, to prevent ignition of combustible materials? |  |  |  |
| 14 | Fire Safety Plan {7.1}: Has a fire safety plan been established and has a Fire Prevention Program Superintendent been designated? |  |  |  |
| 15 | Fire Alarms {7.4}: |  |  |  |
|  | Is there a readily available pull box for fire alarms? |  |  |  |
|  | If a telephone is used, are instructions clearly posted? |  |  |  |
| 16 | Command Post/Evac Area {7.5} |  |  |  |
|  | Is there a designated command post provided with plans, emergency info., keys, communication, and other equipment as needed? |  |  |  |
|  | Is there a clear post-evacuation muster location? |  |  |  |
| 17 | Fire Access {7.5}: |  |  |  |
|  | Are pre-approved fire department access routes being maintained? |  |  |  |
|  | Is there clear access to hydrants, standpipe and fire department connections? |  |  |  |
| 18 | Standpipes {7.6, 8.7.4}: Are standpipes ready for use, and remain within one floor of the top-level during construction/demolition? |  |  |  |
| 19 | Egress {7.8}: Is the means of egress acceptable (e.g. properly marked, clear, safe, lighted)? |  |  |  |
| 20 | Sprinkler {8.7.3}: |  |  |  |
|  | Is the sprinkler in place as soon as practicable following construction? |  |  |  |
|  | Are sprinkler valves checked at the end of each shift? |  |  |  |
| 21 | Fire Cutoffs {8.6.1}: |  |  |  |
|  | Are fire walls and exit stairwells, where required for the completed building, given construction priority for installation? |  |  |  |
|  | Are fire doors installed as soon as practicable? |  |  |  |
| 22 | Stairs {7.5.6}: Is a stairwell provided for the building? |  |  |  |
|  | Is the stairwell extended upward as each floor is installed in new construction and maintained for each floor still remaining in demolition? |  |  |  |
|  | Is it lighted? |  |  |  |
|  | Is it enclosed when the building exterior walls are in place? |  |  |  |
|  | Is signage provided indicating floor level, stair designation, and exit path directions? |  |  |  |
|  | Are extinguishers provided at each floor? |  |  |  |
| 23 | Impairments to fire protection systems or fire alarm, detection or communication systems {7.2.4.6}: |  |  |  |
|  | Are temporary impairments of all fire protection devices and alarm/detection systems immediately removed upon completion of work in the area and at the end of each shift? |  |  |  |
|  | Is there an impairment coordinator? |  |  |  |
| Number of Violations: |  |  |  |  |

Notes:

Completed Report Submission Information:

Distribution: Contractor, Campus, CEO, Project File

Submitted to:

Submission Date:

Reviewer:	Date of Review: